## Slide 1: Unit 3: Faults in Transformers and Diagnosis (12L + 4P hours)

## Slide 2: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Outlines:
Review of Transformer Construction and Operation, Behavior of Normal Transformer, Transformer Condition Indicators.
Insulation Classes, Cooling Systems, Thermal performance of transformers: heating at constant load, heating under variable load, insulation wear and load capacity, overload;
Transformer faults: main causes, core faults, winding faults, switching failures, tanks fault, other failures;
Transformer testing and fault diagnostics: HVPD tests, Acoustic detection, short-circuit and open-circuit impedance measurement, frequency-response analysis, Polarization index, measurement of DC resistance, tan-delta tests, Dissolved Gas Analysis;
Fault simulation exercise and laboratory demonstration.

## Slide 3: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
1. Review of Transformer Construction and Operation, Behavior of Normal Transformer, Transformer Condition Indicators.
Figure 1: Construction of Single Phase Transformer
Source: https://omgfreestudy.com/construction-of-transformer-and-transformer-parts/

## Slide 4: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Review of Transformer Construction and Operation, Behavior of Normal Transformer, Transformer Condition Indicators.
Home work 1
1. List down all the parts of transformer and write its function briefly.

## Slide 5: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Review of Transformer Construction and Operation, Behavior of Normal Transformer, Transformer Condition Indicators.
Figure 2: Position of Float Switch under normal condition
During normal operating condition, the float switch are positioned as shown in Figure 2.
There are two Switches, Upper switch and lower switch.
Upper switch is the alarm switch .
Lower switch is the trip switch.
The purple colour shown in the Figure 2 is the mercury.
Mercury, the liquid metal and which is a good conductor of electricity.
Mercury
Gas flow

## Slide 6: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Review of Transformer Construction and Operation, Behavior of Normal Transformer, Transformer Condition Indicators.
Figure 3: Fault has occurred and Buchholz relay is under operation
Internal fault has occurred and gas is generated.
As gas travel from transformer main tank to conservator tank, in between the Buchholz relay tank is located.
The gas accumulates in the upper portion of the Buchholz relay tank, it will displace the oil and float switch move downward short circuiting the alarm circuit as shown in Figure 3.
Once alarm circuit is activated, the operator will come to restore the fault condition.

## Slide 7: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Review of Transformer Construction and Operation, Behavior of Normal Transformer, Transformer Condition Indicators.
Suppose, the operator is late to attain the faulty event in the transformer, the prolong fault will damage the transformer itself.
Therefore, the trip circuit is also provided, which will operate during sever internal faults of transformers.
Trip switch will operate the relay switch is energized which will isolate the transformer from the faulty event.

## Slide 8
In Pursuit of Preparing Tomorrow's Technologists!
The Junk of words “God”, “belief”, “faith”, “money” and “desire” has completely corrupted our brains, thus, if you want to clean it up, start looking for the truth.
Core Type
Construction:
Shell Type
Construction:
Figure 4: Core type Construction of Transforemer
Source:
https://eepower.com/technical-articles/transformer-core-design-and-cooling/#

## Slide 9
In Pursuit of Preparing Tomorrow's Technologists!
The Junk of words “God”, “belief”, “faith”, “money” and “desire” has completely corrupted our brains, thus, if you want to clean it up, start looking for the truth.
Core Type
Difference:
Conductors or winding surrounds the core of transformer.
Stampings are in L-type cut
Cross-section of core is square shaped.
More weight of copper conductor is required.
Losses are more because of more copper conductors.
Only two limbs
Two magnetic circuit
Maintenance is easy.
Shell Type
Core surrounds the winding of the transformer.
Stampings are in E-type cut
Cross-section is rectangular in shaped.
Less weight of copper conductor is required.
Losses are less because of less copper conductors.
Three limbs
One magnetic circuit.
Maintenance is difficult

## Slide 10
Principle of Operation Transformer
A transformer is the static device which changes the alternating voltage from one level to another.
Figure 5, shows the connection diagram of transformer.
It consist of a magnetic core and two distinct windings wound over the core.
Two winding forms two independent electrical circuits where as the core forms a magnetic circuit which is common to both the windings.
The basic principle of transformer is “Mutual induction” between two circuit linked by a common magnetic circuit.
In Pursuit of Preparing Tomorrow's Technologists!
The Junk of words “God”, “belief”, “faith”, “money” and “desire” has completely corrupted our brains, thus, if you want to clean it up, start looking for the truth.

## Slide 11
In Pursuit of Preparing Tomorrow's Technologists!
The Junk of words “God”, “belief”, “faith”, “money” and “desire” has completely corrupted our brains, thus, if you want to clean it up, start looking for the truth.
Figure 5: Connection diagram of transformer

## Slide 12
If one winding is connected to AC supply, an alternating flux is established in the core due to alternating current.
Most of this flux links with the other windings.
This produce mutually induced e.m.f. in that winding.
If circuit of second winding is closed, a current flow on it and therefore electrical energy is transformed from first winding to second winding.
Here the input and out put frequency is constant (i.e. frequency of supply voltage at primary side and frequency of induced voltage at secondary side is same).
The first winding which is connected to supply side is called primary winding whereas other winding to which load is connected is called secondary winding.
In Pursuit of Preparing Tomorrow's Technologists!
The Junk of words “God”, “belief”, “faith”, “money” and “desire” has completely corrupted our brains, thus, if you want to clean it up, start looking for the truth.

## Slide 13
Types of Transformer
Transformer are classified on the basis of:
Duty They Perform
1. Power Transformer (for power transmission purpose)
2. Distribution Transformer (for power distribution purpose)
3. Current Transformer (for instrumentation purpose, measure current )
4. Potential Transformer (for instrumentation purpose, measure voltage)
ii) Construction
1. Core Type Transformer
2. Shell Type Transformer
3. Berry Type Transformer
In Pursuit of Preparing Tomorrow's Technologists!
The Junk of words “God”, “belief”, “faith”, “money” and “desire” has completely corrupted our brains, thus, if you want to clean it up, start looking for the truth.

## Slide 14
iii) Voltage Output
1. Step down Transformer ( higher voltage to lower voltage)
2. Step up Transformer (Lower Voltage to higher Voltage)
3. Auto Transformer (Variable from ‘0’ to rated value)
iv) Application Transformer
1. Welding transformer
2. Furnace Transformer
v) Cooling
1. Duct type Transformer (Air natural or air blast)
In Pursuit of Preparing Tomorrow's Technologists!
The Junk of words “God”, “belief”, “faith”, “money” and “desire” has completely corrupted our brains, thus, if you want to clean it up, start looking for the truth.

## Slide 15
2. Oil Immersed
a. Self cooled
b. Forced air cooled
c. Water cooled
d. Forced oil cooled
vi. Input Supply
1. Single phase Transformer
2. Three phase Transformer
a. Star-star
b. Star - delta
In Pursuit of Preparing Tomorrow's Technologists!
The Junk of words “God”, “belief”, “faith”, “money” and “desire” has completely corrupted our brains, thus, if you want to clean it up, start looking for the truth.

## Slide 16
c. Delta – delta
d. Delta – start
e. Open delta
f. Scott Connection (The Scott-T Connection is the method of connecting two single phase transformer to perform the 3-phase to 2-phase conversion and vice-versa. The two transformers are connected electrically but not magnetically. One of the transformers is called the main transformer, and the other is called the auxiliary or teaser transformer.)
In Pursuit of Preparing Tomorrow's Technologists!
The Junk of words “God”, “belief”, “faith”, “money” and “desire” has completely corrupted our brains, thus, if you want to clean it up, start looking for the truth.

## Slide 17: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Behavior of Normal Transformer
When transformer is working under the normal condition, it exhibits the following:
Primary and Secondary Windings:
When an alternating current (AC) flows through the primary winding, it creates a time-varying magnetic field in the transformer core.
This magnetic field induces a voltage in the secondary winding through electromagnetic induction.
2. Step-Up and Step-Down:
Depending on the turns ratio between the primary and secondary windings, transformers can either step up (increase) or step down (decrease) the voltage levels.
The voltage ratio between the primary and secondary sides is directly proportional to the ratio of the number of turns in the windings.

## Slide 18: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Behavior of Normal Transformer
3. Inverse Proportionality:
While transformers change voltage levels, they also inversely change the current levels.
If the transformer steps up the voltage, it steps down the current and vice versa, according to the principle of conservation of energy (neglecting losses).
4. High Efficiency:
Transformers are highly efficient devices, often achieving efficiencies above 95%.
However, some energy is lost as heat due to core losses (hysteresis and eddy currents) and winding losses (I²R losses).

## Slide 19: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Behavior of Normal Transformer
5. Voltage Regulation:
The change in secondary voltage from no-load to full-load conditions is called voltage regulation.
Ideal transformers have low voltage regulation, meaning their output voltage remains relatively constant regardless of the load.
6. Magnetizing Current:
A small magnetizing current flows through the primary winding to establish the magnetic field in the core even when there is no load on the secondary winding.

## Slide 20: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Behavior of Normal Transformer
7. Hysteresis and Eddy Current Losses:
These are losses in the transformer core due to the alternating nature of the magnetic field.
Hysteresis losses are due to the lagging behavior of magnetic domains in the core material, and eddy current losses are due to circulating currents induced in the core.
8. Load Dependence:
The secondary voltage of a transformer decreases slightly as the load increases due to the internal impedance of the transformer.
This behavior is quantified by the transformer's voltage regulation.

## Slide 21: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Transformer Condition Indicators
1. Temperature Indicators
Oil Temperature: Measures the temperature of the transformer oil. High temperatures can indicate excessive loading or cooling system failure.
Winding Temperature: Indicates the temperature of the transformer windings. Excessive winding temperature can lead to insulation degradation.
2. Oil Quality Indicators
Dissolved Gas Analysis (DGA): Measures the concentration of gases dissolved in the transformer oil. Certain gases (e.g., hydrogen, methane, ethylene) can indicate various types of faults, such as arcing, overheating, or insulation breakdown.
Oil Dielectric Strength: Assesses the insulating properties of the transformer oil. Low dielectric strength can indicate contamination or degradation of the oil.
Moisture Content: High moisture levels in the oil can reduce its insulating properties and lead to accelerated aging of the insulation.

## Slide 22: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Transformer Condition Indicators
3. Load Indicators
Load Current: Monitors the current flowing through the transformer. Consistently high load currents can lead to overheating and accelerated aging.
Power Factor: Measures the power factor of the load. Low power factor can indicate inefficient operation and higher losses.
4. Physical and Visual Inspections
Bushing Condition: Inspects the physical condition of the bushings for cracks, contamination, or oil leaks. Damaged bushings can lead to electrical faults.
Physical Deformation: Checks for any signs of physical deformation or damage to the transformer tank and components.
Oil Leaks: Identifies any oil leaks, which can lead to reduced insulation and cooling efficiency.

## Slide 23: Develop the practice of thinking positively because our minds are typically more predisposed to thinking negatively.
Transformer Condition Indicators
5. Buchholz Relay
Gas Accumulation: Detects the accumulation of gases in the relay, which can indicate internal arcing or severe overheating.
Oil Flow: Monitors the flow of oil through the relay, which can indicate oil leaks or cooling system issues.
6. Cooling System Performance
Cooling Fans and Pumps: Monitors the operation of cooling fans and pumps. Malfunctioning cooling systems can lead to overheating.
Radiator Temperature: Measures the temperature of the radiator to ensure effective heat dissipation.

## Slide 24: As learners, we must put more of an emphasis on LISTENING than on working alone!
References: