## Slide 1: Unit 3: Faults in Transformers and Diagnosis (12L + 4P hours)

## Slide 2: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Outlines:
Review of Transformer Construction and Operation, Behavior of Normal Transformer, Transformer Condition Indicators.
Insulation Classes, Cooling Systems, Thermal performance of transformers: heating at constant load, heating under variable load, insulation wear and load capacity, overload;
Transformer faults: main causes, core faults, winding faults, switching failures, tanks fault, other failures;
Transformer testing and fault diagnostics: HVPD tests, Acoustic detection, short-circuit and open-circuit impedance measurement, frequency-response analysis, Polarization index, measurement of DC resistance, tan-delta tests, Dissolved Gas Analysis;
Fault simulation exercise and laboratory demonstration.

## Slide 3: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Insulation Classes, Cooling Systems, Thermal performance of transformers: heating at constant load, heating under variable load, insulation wear and load capacity, overload;
Why insulation is used in electrical system?
To achieve the intended direction of current.
An insulating materials should have following properties:
high resistivity,
high dielectric strength,
low dielectric loss,
withstand heat,
sufficient mechanical strength to withstand strong vibration of machine, and
Should be non-hygroscopic in nature.

## Slide 4: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
The insulating materials used in electrical machines are:
cotton,
varnishes,
cloths,
silks,
rubbers,
bakelite,
paper,
wood,
mica,
asbestos,
glass,
porcelain,
insulating oil (Paraffins, naphthene and aromatic etc.)

## Slide 5: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Classification of insulating materials:
Insulating materials are always subjected to heat in the electrical circuits. Therefore, it is good idea to classify the insulating martials into different classes based on their limiting temperature capabilities.
Class Y
Cotton yarns and fabrics, paper and fibrous materials of cellulose or silk.
Limiting temperature is 90°.
2. Class A
Same materials as above but impregnated with immersed in liquid dielectric.
Limiting temperature is 105°.
3. Class E
Certain synthetic organic films.
Limiting temperature is 120°.

## Slide 6: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
4. Class B
Mica, asbestos, or glass-fibre base materials combined with organic binding.
Limiting temperature is 130°.
5. Class F
Mica, Asbestos or glass-fibre combined with suitable synthetic binding and impregnated agent.
Limiting temperature is 155°.
6. Class H
Mica, asbestos or glass fibre combined with silicon binding and impregnated agent.
Limiting temperature is 180°.
7. Class C
Mica, ceramic materials, glass or quartz used with inorganic binding agents.
Limiting temperature is 180° and above.

## Slide 7: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Note: Temperature limits of any electrical machine should not be exceeded in practice, if temperature limit is exceeded then it will result in deteriorations and breakdown in insulations and will shorten the life of machines.

## Slide 8: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Insulation Classes, Cooling Systems, Thermal performance of transformers: heating at constant load, heating under variable load, insulation wear and load capacity, overload;
Cooling of Transformer
In the process of transformation of energy from one voltage level to another voltage level some energy is lost in between, in the core and in the windings.
The energy loss in transformer increases with increase kVA rating/capacity of the transformer.
All energy lost in the transformer must be dissipated as heat.
There are number of methods for cooling of transformers.
The choice of methods of cooling depends upon the size, type of application and type of conditions available at the site where the transformer is installed.
In general the transformers are categories as “Dry type” or “Oil Immersed type”.

## Slide 9: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
The cooling method used for dry type transformer are:
Air Natural (AN) cooling.
For smaller output (5-10 kVA) the external surface is sufficient to dissipate the heat produced by losses.
Instrument transformers, except for those for the highest voltages, are ordinarily of dry types.
Dry-type transformer are frequently used indoor since it is not necessary to install them in fire proof domes.

## Slide 10: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
2. Air Blast Cooling.
In this type of cooling, heat dissipation is improved by a continuous blast of air forced through the core of windings.
Air blast is produced by means of external fans or blowers.
This type of cooling is done in transformers whose rating is 25 kVA and below.
It is used in situation located in thickly populated places where oil is considered as a fire hazard.

## Slide 11: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Cooling method used in oil immersed type of transformer:
Oil natural cooling.
This is the most usual method of cooling.
Here assembly of core and windings are immersed in the insulating oil contained in iron tank.
The heat produced in core and windings is passed onto the coil by conduction.
The heated oil transfers its heat to the tank surface which dissipates it to the surroundings.
Advantages of this method of cooling are:
Freedom from dust
Freedom from atmospheric moisture which would have affected the insulation.
Easy extraction of heat from innermost parts as oil is better conductor of heat.
Good amount of natural convection currents since oil has high coefficient of volume of expansion.
For further increasing the heat dissipating capacity, radiators or tubes are provided on all the four walls of the transformer.

## Slide 12: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
2. Oil Natural Air Forced (ONAF) cooling.
Here again the assembly of core and windings is immersed in an insulating oil and cooling is improved by forced air over the cooling surface.
The air is forced over external surface such as case, tubes, and radiators, usually by means of fans mounted external to the transformer.
Medium to large transformer are cooled by this method.
3. Oil Natural Water Forced (OLWF) cooling.
For such cooling, the core and winding are immersed in an insulating oil and cooling is increased by circulation of water through a copper cooling coils mounted above the transformer core but below the oil surface level.
The heated water is cooled in a cooling tower.

## Slide 13: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
5. Oil Forced Air natural (OFAN) cooling.
In this method of cooling, oil is circulated through the transformer with help of pump and cooled in a heat exchanger by natural circulation of air.
6. Oil forced Air forced (OFAF) cooling.
In this method of cooling, the oil is cooled in external heat exchanger usig air blast produced by fan.
At higher loads more heating is produced, the pump and fans may be switched ‘ON’ by temperature sensing elements.

## Slide 14: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
6. Oil Force Water Forced (OFWF) Cooling.
In this method of cooling, heated oil is pumped out from the main tank the radiator (heat exchanger) where oil is cooled by water passing through copper tubes.
Pressure of oil is maintained higher than that of water, so that oil will leak into the water not water leaking into the oil.
OFWF cooling system is done in the transformer whose rating are above 30 MVA.

## Slide 15: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Insulation Classes, Cooling Systems, Thermal performance of transformers: heating at constant load, heating under variable load, insulation wear and load capacity, overload;
Thermal performance of transformers
The thermal performance of a transformer is critical for its efficiency, reliability, and longevity.
It involves analyzing how well the transformer can dissipate the heat generated during operation.
Excessive heat can lead to insulation degradation, reduced lifespan, and potential failures.

## Slide 16: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Heat generation in transformer is mainly due to the following losses:
Core losses (hysteresis losses and eddy current losses),
hysteresis losses occurs in the core of transformers due to repeated magnetization and demagnetization in the core.
Eddy current losses occurs due to the circulation of current in the core of the electrical machines.
2. Copper Losses (I²R Losses):
Copper losses occur due to the resistance in the windings and vary with the percentage of loading on the transformers.
Higher copper losses when transformer is heavily loaded and less copper losses when transformer is loaded lightly.

## Slide 17: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
It's clear that transformers generate heat, so we must address and reduce the heat build-up through careful thermal design considerations.
When the transformer operates under a steady load for a sufficient duration, a steady temperature is established at every point.
The hottest point in the transformer is typically at the top of the winding inside it, where the temperature is 2-3°C higher than the temperature at the outer surface of the winding.

## Slide 18: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Electrical transformers are well design to counter the heat rise in it, here are few key aspect design in transformers to suppress the heat rise.
Heat Dissipation Components:
Radiators, fans, pumps (in oil-cooled transformers), and cooling fins.
2. Insulation System:
The type and quality of insulation used in the windings and core to withstand high temperatures.
3. Load Factor:
The relationship between the actual load and the rated load of the transformer.
Higher loads generate more heat.

## Slide 19: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Heating of Transformer at Constant Load
Heating at a constant load in a transformer is a critical aspect to understand for maintaining the efficiency and longevity of the equipment.
At a constant load, the heating characteristics are influenced by the continuous power losses within the transformer, primarily due to copper and core losses.
Copper losses are proportional to the square of the load current and are constant for a given load.
Core losses are constant as long as the voltage and frequency remain constant, regardless of the load.
The transformer needs to dissipate the heat generated by these losses to maintain a stable operating temperature. This is achieved through various cooling methods.

## Slide 20: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Heating of transformer under variable load
Unlike a constant load, variable load conditions can introduce additional complexities in the thermal management of the transformer.
Here’s a detailed explanation of the heating effects and key factors influencing heating under variable Load:

## Slide 21: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Load Cycles:
Transformers often experience fluctuations in load due to changes in demand.
These fluctuations can range from light load to full load conditions, and contributing to the heating nonuniformly.
When the load changes, the temperature of the transformer also changes.
The calculation of temperature change involves replacing the transformer, consisting of the core, windings, transformer oil, and casing, with an equivalent mass of a solid body.
The equations for the heating of a homogeneous solid body are then used.

## Slide 22: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
In this process, it is assumed that heat is uniformly distributed over the entire mass.
In the case where the load increases abruptly from a value of K1 to a value of K2, the steady-state temperature of the transformer oil rises from to .
Figure 1: Relationship between variable load and temperature rise

## Slide 23: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
2. Copper Losses:
These losses, which are proportional to the square of the load current (I²R losses), will vary with the load.
As the load increases, copper losses increase, leading to more heat generation.
3. Core Losses:
Unlike copper losses, core losses (hysteresis and eddy current losses) are relatively constant as they depend mainly on the voltage and frequency, not the load.
4. Thermal Inertia:
The transformer has a certain thermal inertia due to its mass and the cooling medium.
This means it does not instantly reach a new temperature when the load changes but instead heats up or cools down over time.

## Slide 24: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
6. Cooling System Efficiency:
The effectiveness of the cooling system (air-cooled, oil-cooled, etc.) in dissipating heat will influence the temperature rise under varying loads.
Note:
Transient Thermal Behavior:
When the load changes, the temperature of the transformer will also change, but not immediately.
There is a lag due to the thermal inertia, which causes the transformer to heat up or cool down gradually.

## Slide 25: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
6. Cooling System Efficiency:
The effectiveness of the cooling system (air-cooled, oil-cooled, etc.) in dissipating heat will influence the temperature rise under varying loads.
Note:
Transient Thermal Behavior:
When the load changes, the temperature of the transformer will also change, but not immediately.
There is a lag due to the thermal inertia, which causes the transformer to heat up or cool down gradually.

## Slide 26: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Insulation Wear and Load Capacity,
Insulation wear refers to the degradation of the insulating materials within a transformer over time.
Insulating materials are essential to prevent short circuits, ensure efficient energy transfer, and maintain transformer reliability.
1. Causes of Insulation Wear:
Thermal Stress: High temperatures can accelerate the aging of insulation.
Electrical Stress: High voltage and current can cause dielectric breakdown.
Mechanical Stress: Vibrations and mechanical forces can cause physical damage.
Environmental Factors: Moisture, chemicals, and pollutants can degrade insulation.

## Slide 27: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
2. Effects:
Reduced Efficiency: Degraded insulation can increase energy losses.
Increased Risk of Failure: Insulation wear can lead to short circuits or transformer failure.
Maintenance and Downtime: Regular maintenance is needed to monitor and replace worn insulation.
3. Monitoring and Mitigation:
Regular Testing: Conducting dielectric and insulation resistance tests.
Temperature Control: Using cooling systems to manage temperature.
Moisture Control: Employing dehumidifiers and maintaining dry conditions.
Material Upgrades: Using advanced insulating materials with better thermal and mechanical properties.

## Slide 28: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Load Capacity of Transformers
Load capacity refers to the maximum electrical load a transformer can handle without exceeding its thermal limits or compromising its operational integrity.
1. Calculation of Load Capacity:
Nameplate Rating: Provided by the manufacturer, indicating the maximum load under standard conditions.
Thermal Limits: Based on the maximum allowable temperature rise.
Load Profile Analysis: Evaluating the typical load variations and peak loads.

## Slide 29: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
2. Impact of Exceeding Load Capacity:
Overheating: Can lead to accelerated insulation wear and potential failure.
Efficiency Loss: Higher losses and reduced efficiency.
Shortened Lifespan: Increased wear and tear on transformer components.
3. Management Strategies:
Load Balancing: Distributing load evenly across multiple transformers.
Capacity Upgrades: Installing transformers with higher capacity if necessary.
Real-time Monitoring: Using sensors and IoT devices to monitor load and temperature in real-time.

## Slide 30: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Transformer rated power ( ) refers to the apparent power with which the transformer can operate without interruption under nominal parameters throughout its designated operational life.
In reality, transformers rarely operate under constant load.
If Smax is chosen to be equal to , then the transformer temperature will never reach the rated value.
This implies uneconomical use of transformer materials.
From an economic standpoint, it is better to choose ≤ .
The determination of the transformer's load capacity is based on the aging of insulation.

## Slide 31: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Overload of Transformer
Overload in a transformer refers to a condition where the transformer is subjected to an electrical load exceeding its rated capacity.
1. Causes of Overload
Increased Demand: Unexpected or sustained rise in electrical demand beyond the initial design specifications.
Fault Conditions: Short circuits or other electrical faults leading to a surge in load.
Improper Sizing: Using a transformer that is not appropriately sized for the intended load.
Parallel Operation Issues: Inefficiencies or imbalances when multiple transformers operate in parallel, causing one to bear more load than it should.

## Slide 32: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
2. Effects of Overload
Overheating: Excessive load leads to increased current, which generates more heat. Prolonged overheating can degrade insulation and other components.
Insulation Degradation: High temperatures accelerate the aging of insulating materials, reducing their effectiveness and increasing the risk of electrical failures.
Reduced Efficiency: Overloaded transformers operate less efficiently, resulting in higher energy losses.
Mechanical Stress: Excessive load can cause physical stress on windings and other components, leading to mechanical failures.
Shortened Lifespan: Continuous overload can significantly reduce the transformer's operational life, necessitating earlier replacement.

## Slide 33: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
3. Signs of Overload
Temperature Rise: Unusual increase in transformer temperature, detectable through sensors or infrared imaging.
Noise and Vibrations: Increased noise levels or vibrations, indicating mechanical stress.
Decreased Voltage: Voltage drops due to excessive current draw.
Frequent Tripping: Protective devices like circuit breakers or fuses tripping more often than usual.

## Slide 34: Up until now, our grasp of reality is confined to bodily experiences, yet there remains a need to comprehend the conscious reality.
Overload of Transformer
The necessary information can be obtained only through continuous monitoring of the transformer's operation.
For this purpose, load monitoring devices connected to the general information network of the electrical system should be installed on the transformer, along with temperature sensors for the cooling environment.
Temperature sensors enabling continuous monitoring should also be installed within the transformer to account for various additional factors such as solar radiation, changes in thermal conductivity due to insulation aging, etc.
Installing monitoring devices on all transformers may not be economically feasible.
Nowadays, instead of continuous monitoring, determining overload capacities that allow normal operation of the transformer is more common.
The goal is to find the optimum conditions of loads and external environmental factors where the rate of insulation aging matches the overload capacity of transformers.

## Slide 35: As learners, we must put more of an emphasis on LISTENING than on working alone!
References:
Bimbhra, P. (2013). Electrical Machinery. Krishna Nagar, Delhi: Khanna Publisher. Retrieved from www.khannapublishers.in
J.B.Gupta. (2007). Theory and Performance of Electrical Machines (Fourteen Edition ed.). Nai Sarak, Delhi: S.K. Kataria & Sons. Retrieved from katariabooks@yahoo.com
Gnanavadive, J., Prabha, N. R., Kumar, C. S., & Kannan, P. (2005). Electrical Machines. Chennai: M. sethuraaman, Anuradha Agencies, Publishers.