## Slide 1: Unit 3: Faults in Transformers and Diagnosis (12L + 4P hours)

## Slide 2: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Outlines:
Review of Transformer Construction and Operation, Behavior of Normal Transformer, Transformer Condition Indicators.
Insulation Classes, Cooling Systems, Thermal performance of transformers: heating at constant load, heating under variable load, insulation wear and load capacity, overload;
Transformer faults: main causes, core faults, winding faults, switching failures, tanks fault, other failures;
Transformer testing and fault diagnostics: HVPD tests, Acoustic detection, short-circuit and open-circuit impedance measurement, frequency-response analysis, Polarization index, measurement of DC resistance, tan-delta tests, Dissolved Gas Analysis;
Fault simulation exercise and laboratory demonstration.

## Slide 3: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
DIAGNOSTICS

## Slide 4: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
1. High-voltage Partial Discharge (HVPD) Tests
High-voltage partial discharge (HVPD) tests along with electrical and acoustic detection.
This measurement is the most meaningful test for identifying local faults in insulation.
HVPD (High Voltage Partial Discharge) tests in transformers are diagnostic tests used to detect and measure partial discharges within the transformer insulation system.
Partial discharge (PD) is a localized dielectric breakdown of a small portion of the insulation under high voltage stress, which does not completely bridge the space between conductors.
Over time, PD can deteriorate insulation, leading to insulation failure and transformer breakdown.
Figure1: Partial Discharge

## Slide 5: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
1. Purpose of PD Test:
To detect and locate partial discharges within the transformer.
To assess the condition of the insulation system.
To predict potential failures and plan maintenance.
2. Types of HVPD Tests:
Offline PD Testing: Performed when the transformer is de-energized. It allows for a controlled environment and more sensitive detection of PD.
Online PD Monitoring: Performed while the transformer is in service. It provides continuous monitoring and real-time data, allowing for early detection of PD activity.

## Slide 6: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
3. Test Methods:
Electrical Method: Measures the electrical pulses generated by PD activity.
Acoustic Method: Detects sound waves generated by PD activity using ultrasonic sensors.
Ultraviolet (UV) Method: Uses UV cameras to detect UV light emitted by PD activity.
Chemical Method: Analyzes gases
4. Benefits:
Early detection of insulation defects.
Improved reliability and lifespan of the transformer.
Reduced risk of unexpected failures and outages.
Cost-effective maintenance planning.

## Slide 7: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Figure 2: Partial discharge measurement circuit, as per IEC 60270
Supply generator
Supply transformer
Test transformer
Voltage transformer and measuring circuit
Filter
Measuring impedance
Selective switch
Measuring instrument and oscilloscope
qo – calibration generator
https://electrical-engineering-portal.com/transformer-routine-test-partial-discharge-measurement

## Slide 8: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
2. Short-circuit and open-circuit impedance measurement test
Short-circuit and open-circuit impedance measurements are critical tests for characterizing the electrical properties of transformers.
These measurements help in determining the equivalent circuit parameters, which are essential for analyzing transformer performance under different load conditions.
Short-circuit and open-circuit impedance measurements allow the detection of faults in windings and the core.
To determine the impedance of the transformer when the secondary winding is open-circuited.
This test provides information about the magnetizing inductance and core losses.
To determine the impedance of the transformer when the secondary winding is short-circuited.
This test provides information about the winding resistance and leakage reactance.

## Slide 9: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Figure 3: Circuit connection for Open-circuit and short-circuit test

## Slide 10: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.

## Slide 11: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
3. Frequency response analysis –FRA.
Frequency Response Analysis (FRA) is a method used to characterize the behavior of systems, components, or structures in response to a range of frequencies.
It involves analyzing how a system responds to sinusoidal inputs at various frequencies.
FRA is commonly used in engineering fields like control systems, mechanical engineering, and electrical engineering to understand the dynamic characteristics of a system.
The analysis of amplitude-frequency characteristics is a comparative method that reveals geometric changes caused by a short circuit or vibration in the windings.

## Slide 12: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Steps to perform FRA:
1. Preparation:
Isolate the transformer from the electrical network.
Ensure safety procedures are followed to prevent accidents.
2. Connect Test Equipment:
Connect the FRA equipment to the transformer's terminals.
Typically, measurements are taken between the high voltage (HV) and low voltage (LV) windings, and between windings and the ground.
3. Apply the Input Signal:
A low voltage, sinusoidal signal is applied over a wide frequency range (typically from a few Hz to several MHz).

## Slide 13: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
4. Measure the Output:
Record the transformer's output response at each frequency.
Measurements are taken in terms of magnitude and phase angle of the response.
5. Analyze the Data:
Plot the Frequency Response (Bode Plot) showing magnitude and phase against frequency.
Compare the plots with baseline data (either from the same transformer at a previous time or from a similar transformer).
6. Interpret the Results:
Identify significant deviations from the baseline.
Characterize the type and location of the fault based on the nature of the deviations.
  Shift in Resonance Peaks: Indicate mechanical displacement or deformation.
  Changes in Magnitude: Suggest shorted turns or open circuits.
  Phase Angle Variations: Point to core or winding issues.

## Slide 14: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
4. Polarization Index (PI) test
The Polarization Index (PI) test is an important diagnostic tool for assessing the condition of insulation in transformers and other electrical equipment.
It helps to evaluate the insulation's dryness, cleanliness, and overall health by measuring the resistance of the insulation over a period of time.
The Polarization Index is the ratio of the insulation resistance measured over 10 minutes to the insulation resistance measured over 1 minute.
The formula is:
where ​ is the insulation resistance after 10 minutes and ​ is the insulation resistance after 1 minute.

## Slide 15: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Steps to Conduct the PI Test
Preparation:
  Ensure the transformer is de-energized and properly grounded.
  Disconnect any connected load or equipment.
  Clean the surface of the insulation to remove any dirt or moisture.
Testing:
  Connect the insulation resistance tester (megger) between the winding and ground.
  Start the test and record the insulation resistance at 1 minute () and at 10 minutes ().
  Calculate the Polarization Index using the formula:
Interpretation of Results:
  < 1: Poor insulation, indicates contamination or moisture presence.
  1 ≤ < 2: Marginal insulation, needs further investigation or immediate maintenance.
  2 ≤ ≤ 4: Good insulation, acceptable condition.
  > 4: Excellent insulation, typically for new or well-maintained equipment

## Slide 16: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
5. Polarization and depolarization currents. This method is used for determining polarizable substances in insulation. It enables the assessment of water content in the pressboard.
6. Measurement of direct current resistance. This measurement detects short circuits and changes in resistance. It also allows for the determination of contact resistances. Recording the switching operations of load-tap changers (dynamic measurement) under load helps assess whether the contacts switch correctly.

## Slide 17: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
5. Tan-Delta Test
What is the Tan-Delta Test?
The tan-delta (δ) is a measure of the dielectric loss of the insulation system.
It represents the phase angle difference between the applied voltage and the resulting current in the insulation.
A higher tan-delta value indicates higher dielectric losses and potentially deteriorating insulation.
Importance of the Tan-Delta Test
Insulation Quality Assessment: It helps in evaluating the quality and integrity of the transformer insulation.
Aging and Degradation Monitoring: It can detect insulation aging and degradation over time.
Preventive Maintenance: Early detection of insulation issues can prevent unexpected failures and extend the lifespan of the transformer.

## Slide 18: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Steps to Perform the Tan-Delta Test
Preparation:
Ensure the transformer is de-energized and properly grounded.
Clean the insulation surface to remove any contamination or moisture.
Disconnect the transformer from the network and any other connected equipment.
2. Test Setup:
Connect the test equipment (tan-delta test set) to the transformer.
The equipment typically consists of a high-voltage source, a bridge circuit, and a measurement unit.
The test is usually performed on the primary winding (high-voltage side) of the transformer.
Connect the high-voltage lead of the test set to the primary winding and the low-voltage lead to the ground.

## Slide 19: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
3. Testing:
Apply the test voltage (usually between 1 kV and the rated voltage of the transformer) to the primary winding.
Measure the test current and the phase angle between the applied voltage and the current.
The tan-delta value is calculated using the formula:
Where, ​ is the resistive (loss) component of the current and ​ is the capacitive (charging) component of the current.
4. Recording and Interpretation of Results:
Record the tan-delta values at different test voltages.
Compare the measured tan-delta values with the manufacturer’s specifications or industry standards.
Typical interpretation of results:
Low tan-delta (<0.5%): Good insulation condition.
Moderate tan-delta (0.5% - 1.0%): Marginal insulation, may require further investigation.
High tan-delta (>1.0%): Poor insulation, indicates significant degradation or contamination.

## Slide 20: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Figure 4: Circuit connection for performing tan-delta test of the transformer

## Slide 21: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
6. Dissolved Gas Analysis
Dissolved Gas Analysis (DGA) is a key diagnostic tool used to assess the condition of transformer oil and, by extension, the health of the transformer itself.
This analysis involves detecting and quantifying gases dissolved in the transformer oil, which are generated due to thermal and electrical stresses within the transformer.
Oil analysis procedures provide specific information about the insulation condition from multiple aspects: the overall condition of the oil, the composition of dissolved gases, and other processes related to oil aging.

## Slide 22: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Common gases analyzed in DGA include:
Hydrogen ()
Methane ()
Ethane ()
Ethylene ()
Acetylene ()
Carbon Monoxide (CO)
Carbon Dioxide ()

## Slide 23: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Common gases analyzed in DGA include:
Hydrogen ()
Methane ()
Ethane ()
Ethylene ()
Acetylene ()
Carbon Monoxide (CO)
Carbon Dioxide ()
Key Faults Detected by DGA:
Thermal Faults: Overheating of oil or cellulose insulation.
Electrical Faults: Partial discharges, arcing, or corona discharges.
Insulation Breakdown: Degradation of oil and solid insulation.

## Slide 24: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Steps to Perform DGA
Oil Sampling:
Ensure the transformer is in a stable condition before taking the sample.
Use clean, dry, and airtight glass syringes or stainless steel bottles for sampling.
Draw the oil sample from a designated sampling valve, avoiding contamination.
2. Laboratory Analysis:
The oil sample is analyzed in a laboratory using gas chromatography.
The dissolved gases are extracted from the oil sample and injected into a gas chromatograph, which separates and quantifies each gas.
3. Interpretation of Results:
The concentration of each gas is measured in parts per million (ppm).
The results are interpreted using various methods and standards, such as IEEE C57.104, IEC 60599, and Duval’s Triangle.

## Slide 25: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Interpretation:
The presence of hydrogen () and methane () indicates potential thermal issues.
Elevated ethylene () suggests high-temperature overheating.
Low acetylene () indicates the absence of severe arcing.
Elevated carbon monoxide (CO) and carbon dioxide () suggest cellulose insulation degradation.
Using Duval’s Triangle, these results could point to thermal fault T2 (temperature range of 300-700°C), indicating overheating of the oil.

## Slide 26: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Fault simulation exercise and laboratory demonstration.