## Slide 1: Unit 3: Faults in Transformers and Diagnosis (12L + 4P hours)

## Slide 2: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Outlines:
Review of Transformer Construction and Operation, Behavior of Normal Transformer, Transformer Condition Indicators.
Insulation Classes, Cooling Systems, Thermal performance of transformers: heating at constant load, heating under variable load, insulation wear and load capacity, overload;
Transformer faults: main causes, core faults, winding faults, switching failures, tanks fault, other failures;
Transformer testing and fault diagnostics: HVPD tests, Acoustic detection, short-circuit and open-circuit impedance measurement, frequency-response analysis, Polarization index, measurement of DC resistance, tan-delta tests, Dissolved Gas Analysis;
Fault simulation exercise and laboratory demonstration.

## Slide 3: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Transformer faults: main causes, core faults, winding faults, switching failures, tanks fault, other failures;
Playing a crucial role as critical and expensive devices, transformers are essential for the integrity of electrical power and the entire electrical system.
At the same time, transformers have their operational lifespan.
Statistically, two-thirds of damages result from incorrect installation and operation, while one-third is due to manufacturing errors.
Transformer failures can be classified as follows:
Core faults
Winding issues
Thermal damage
Switching faults
Overloading
Mechanical failure
Design and Manufacturing Defects
External Factors
Aging and wear

## Slide 4: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
1. CORE
The core is a fundamental component of transformers, ensuring good inductive coupling between the windings.
The main cause that can lead to core faults is overheating, where high temperatures deteriorate the insulation materials and result in the hardening of the steel laminations.
Another issue is the loosening of the core clamping—fasteners become loose, causing vibrations in the outer layers of the core.

## Slide 5: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
1. CORE
A significant issue for transformers is the aging and wear of insulation.
Prolonged operation of the transformer can lead to insulation wear.
Premature wear is also observed, resulting from frequent overloads or insufficient cooling under rated load.
Cooling conditions may deteriorate due to coil contamination or oil aging.

## Slide 6: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
2. Windings
Failures in insulation can occur due to high humidity.
Issues with windings typically begin with interturn shorts.
If preventive maintenance is not performed, an inter-turn short can escalate to a phase-to-phase or ground short.
Due to the difficulty of preventively detecting this inter-turn short, even in its early stages, it can cause serious damage.

## Slide 7: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
3. Switching
Switch failures are usually associated with the breakage of contacts between the rods under voltage and the moving rings.
This can be caused by the formation of an oxide film on the contact elements' surfaces as well as pressure drops.
In more complex regulators, damages typically occur due to contact burning, weakening of the strength of steel parts, wear of paper-bakelite shafts, or the clogging of contactors.

## Slide 8: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
3. Switching
Main Causes of switching failure in transformers:
Switching surges (slow switching causes arching and voltage surges)
Mechanical Stresses on switch gears
Thermal stresses
Transient over voltages
Contact wares in switchgears
Operational errors

## Slide 9: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
4. Tank
Tank faults can lead to oil loss and abnormal temperature rise.
Possible causes of tank failure include poor-quality welding and insufficiently tightened seals between the tank and the cover.
For repairs, it is necessary to:
Clean the tank
Flush the tank with warm oil
Check the operation of the drain valve
Weld leak points

## Slide 10: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
4. Tank
Main causes of transformer tank failure:
Corrosions
Thermal stresses
Design flaws
Mechanical damages
Manufacturing defects
Maintenance issues
Environmental factors (Seismic damages, extreme weather conditions)

## Slide 11: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
5. Other failures
In addition to the aforementioned damages, abnormal conditions caused by external factors can induce stresses and, consequently, faults in the transformer.
These conditions include:
Overloading: Operating the transformer beyond its rated capacity.
System faults: Issues within the power system that affect the transformer's operation.
Overvoltage: Abnormally high voltages in the system.
Undervoltage operation: Operating the transformer at frequencies lower than normal.

## Slide 12: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
DIAGNOSTICS

## Slide 13: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Methods
1. High-voltage partial discharge tests along with electrical and acoustic detection. This measurement is the most meaningful test for identifying local faults in insulation.
2. Short-circuit and open-circuit impedance measurements allow the detection of faults in windings and the core.

## Slide 14: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Methods
3. Frequency response analysis –FRA. The analysis of amplitude-frequency characteristics is a comparative method that reveals geometric changes caused by a short circuit or vibration in the windings.
4. Measurement of the ratio. This measurement is used to detect various short circuits on a load-regulated tap changer.

## Slide 15: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Methods
5. Polarization and depolarization currents. This method is used for determining polarizable substances in insulation. It enables the assessment of water content in the pressboard.
6. Measurement of direct current resistance. This measurement detects short circuits and changes in resistance. It also allows for the determination of contact resistances. Recording the switching operations of load-tap changers (dynamic measurement) under load helps assess whether the contacts switch correctly.

## Slide 16: Before advising someone to change their characters, behaviors and way of thinking, one must first have mastery of these attributes.
Methods
7. C-tan(δ) bushing measurement. Such a measurement is used to determine the aging conditions of bushing insulation.
8. Oil analysis procedures provide specific information about the insulation condition from multiple aspects: the overall condition of the oil, the composition of dissolved gases, and other processes related to oil aging.

## Slide 17: As learners, we must put more of an emphasis on LISTENING than on working alone!
Thanks to Mrs. Karolina Kudelina for the Notes.